## Report
id | refrigerants | sources | manufacturer | name | series | operation_mode | trl_min | trl_max | trl_description | circuit | n_circuits | circuit_configuration | circuit_infos | sink | min_thermal_capacity | max_thermal_capacity | el_connection_voltage | el_connection_phase | el_connection_frequency | el_connection_power | min_flow_temperature | max_flow_temperature | min_temp_source | max_temp_source | t_hub_max | cop | compressor | n_compressor | filling_quantity | min_load | lifespan | length | width | height | weight | weight_max | weight_description | evaporator_inlet | evaporator_outlet | compressor_regulation | condenser_inlet | condenser_outlet | sound_power | sound_pressure_1m | sound_pressure_10m | installation_type | space_requirements | room_height_requirements | comment | updated | verified | information_source | information_source_archive | information_source_date
524 | R717 (Ammoniak) | Abwärme (Brine/Water), Geothermie (Brine/Water), Umweltwärme (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBH12M-WFAA | Open-type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 371.8 | 380 | 3 | 50 |  |  | 90 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 3800 | 2000 | 2400 |  |  |  | DN100 | DN100 | Drehzahlgeregelt | DN50 | DN50 | [7 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
525 | R717 (Ammoniak) | Abwärme (Brine/Water), Geothermie (Brine/Water), Umweltwärme (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBH16M-WFAA | Open-type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 699.6 | 380 | 3 | 50 |  |  | 90 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4400 | 2200 | 2700 |  |  |  | DN125 | DN125 | Drehzahlgeregelt | DN65 | DN65 | [7 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
526 | R717 (Ammoniak) | Abwärme (Brine/Water), Geothermie (Brine/Water), Umweltwärme (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBH18M-WFAA | Open-type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 1070.3 | 380 | 3 | 50 |  |  | 90 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4700 | 2400 | 2800 |  |  |  | DN150 | DN150 | Drehzahlgeregelt | DN80 | DN80 | [7 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
527 | R717 (Ammoniak) | Abwärme (Brine/Water), Geothermie (Brine/Water), Umweltwärme (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBH20M-WFAA | Open-type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 1399.2 | 380 | 3 | 50 |  |  | 90 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5100 | 2600 | 3000 |  |  |  | DN200 | DN200 | Drehzahlgeregelt | DN100 | DN100 | [7 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
528 | R717 (Ammoniak) | Abwärme (Brine/Water), Geothermie (Brine/Water), Umweltwärme (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBH26M-WFAA | Open-type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 2518.6 | 380 | 3 | 50 |  |  | 90 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5500 | 2800 | 3200 |  |  |  | DN250 | DN250 | Drehzahlgeregelt | DN125 | DN125 | [7 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
536 | R717 (Ammoniak) | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL16M-WDAA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 744.9 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4400 | 2150 | 2650 | 6850 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
530 | R134a | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL16M-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 411 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 3800 | 2250 | 2550 | 6850 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
542 | R134a | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL16M-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 447.6 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 3800 | 2250 | 2550 | 6850 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
548 | R717 (Ammoniak) | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL16M-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 816.9 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4400 | 2150 | 2650 | 6850 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
535 | R717 (Ammoniak) | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL16S-WDAA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 599.5 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4400 | 2100 | 2550 | 6600 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
529 | R134a | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL16S-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 336.9 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 3500 | 2200 | 2450 | 6600 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
541 | R134a | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL16S-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 357 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 3500 | 2200 | 2450 | 6600 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
547 | R717 (Ammoniak) | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL16S-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 657.4 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4400 | 2100 | 2550 | 6600 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
538 | R717 (Ammoniak) | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL20M-WDAA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 1529 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5100 | 2275 | 2855 | 9450 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
532 | R134a | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL20M-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 853.7 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4805 | 2350 | 2800 | 10450 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
544 | R134a | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL20M-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 929.3 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4805 | 2350 | 2800 | 10450 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
550 | R717 (Ammoniak) | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL20M-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 1676.9 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5100 | 2275 | 2855 | 9450 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
537 | R717 (Ammoniak) | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL20S-WDAA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 1182.2 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4900 | 2250 | 2800 | 9200 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
531 | R134a | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL20S-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 610 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4600 | 2300 | 2700 | 9000 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
543 | R134a | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL20S-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 714.8 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4600 | 2300 | 2700 | 9000 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
549 | R717 (Ammoniak) | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL20S-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 1296.4 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4900 | 2250 | 2800 | 9200 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
540 | R717 (Ammoniak) | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL26M-WDAA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 2915.1 | [5 empty] | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5300 | 2400 | 2950 | 18500 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
534 | R134a | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL26M-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 1633.9 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5200 | 2500 | 2950 | 16500 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
546 | R134a | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL26M-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 1778.6 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5200 | 2500 | 2950 | 16500 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
552 | R717 (Ammoniak) | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL26M-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 3196.7 | [5 empty] | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5300 | 2400 | 2950 | 18500 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
539 | R717 (Ammoniak) | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL26S-WDAA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 2315.9 | [5 empty] | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5255 | 2350 | 2930 | 16200 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
533 | R134a | Grundwasser (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL26S-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 1298.8 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5155 | 2460 | 2930 | 16000 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
545 | R134a | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL26S-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 1413.6 | 380 | 3 | 50 |  |  | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5155 | 2460 | 2930 | 16000 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
551 | R717 (Ammoniak) | Wasser/Sole (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBL26S-WDMA | Open-Type Screw Water Source Heat Pump Unit | H&C |  | 9 |  | CLO |  |  |  | Fernwärme, Prozesswärme |  | 2539.4 | [5 empty] | 85 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5255 | 2350 | 2930 | 16200 |  |  |  |  | Drehzahlgeregelt | [9 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
520 | R245fa | Abwärme (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBS12MWF ZANA | Open-type Steam Heat Pump Unit (125℃) | H&C |  | 9 |  | CLO |  |  |  | Prozessdampf |  | 145 | 380 | 3 | 50 |  |  | 125 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 3800 | 2300 | 2500 | 3100 |  |  | DN50 | DN50 | Drehzahlgeregelt | DN32 | DN32 | [7 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
522 | R245fa | Abwärme (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBS16MWF ZANA | Open-type Steam Heat Pump Unit (125℃) | H&C |  | 9 |  | CLO |  |  |  | Prozessdampf |  | 375 | 380 | 3 | 50 |  |  | 125 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4500 | 2300 | 2500 | 3700 |  |  | DN50 | DN50 | Drehzahlgeregelt | DN40 | DN40 | [7 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
521 | R245fa | Abwärme (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBS16SWF ZANA | Open-type Steam Heat Pump Unit (125℃) | H&C |  | 9 |  | CLO |  |  |  | Prozessdampf |  | 297 | 380 | 3 | 50 |  |  | 125 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 4100 | 2300 | 2500 | 3200 |  |  | DN50 | DN50 | Drehzahlgeregelt | DN32 | DN32 | [7 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html
523 | R245fa | Abwärme (Brine/Water) | Fujian Snowman Co., Ltd. (SRMtec) | RBS20SWF ZANA | Open-type Steam Heat Pump Unit (125℃) | H&C |  | 9 |  | CLO |  |  |  | Prozessdampf |  | 586 | 380 | 3 | 50 |  |  | 125 |  |  |  |  | Schraubenverdichter |  |  | 10 |  | 5000 | 2300 | 3000 | 4200 |  |  | DN65 | DN65 | Drehzahlgeregelt | DN40 | DN40 | [7 empty] | 2025-01-16 | FALSE | https://www.srmtec.group/en/product/productlist.html